December 31, 2025

Request For Bids

# ALARM SYSTEM INSPECTIONS & MONITORING

for the: Dakota County CDA

1228 Town Centre Drive Eagan, MN 55123

Contact:

Aaron Davis

Contract Services Coordinator

Dakota County CDA Office: (651) 675-4507

Fax:	(651) 287-8042

adavis@dakotacda.org

| Table of Contents | Page(s) |
| --- | --- |
| Cover Sheet |  |
| Table of Contents | 2 |
| Request for Bids | 3-4 |
| Scope of Work (Alarm System Inspections) | 5-10 |
| Scope of Work (Alarm Monitoring) | 11 |
| Section 3 Requirements | 12 |
| Alarm Systems Inspections Bid Form A | 13-18 (must be returned to CDA) |
| Alarm Monitoring Bid Form B | 19-25 (must be returned to CDA) |
| Contractors Qualification Statement | 26-27 (must be returned to CDA) |
| General Conditions | www.dakotacda.org-doing-business-with-the-CDA/contracting-opportunities/ |
| Sample Contract | www.dakotacda.org-doing-business-with-the-CDA/contracting-opportunities/ |

Submittals to CDA, if awarded a contract

HUD 5369-C Non-Construction Contract	available by request (2 pages)

HUD 5370-C Section 1	available by request (6 pages)

HUD 5370-C Section 2	available by request (3 pages)

HUD 60002 Section 3 Summary Report	available by request (3 pages) Employee & Subcontractor/Independent Contractor List	available by request (1 page)

REQUEST FOR BIDS (RFB)

Alarm System Inspections & Alarm Monitoring

Dakota County CDA, MN

Many areas of this manual have changed so review it carefully. Some of the changes are related to: combining the Alarm System Inspection with the Alarm Monitoring, our property types, our tax-exempt status, and insurance requirements.

Qualified contractors are invited to submit a BID for the above noted services. The contract will be awarded to the qualified contractor with the combined low bid.

Bids due:	Tuesday, January 27th @ 10:00 a.m.

Contract start date:	March 1, 2026 Contract completion:	3-year contract

Contracts will be separated by housing program types

Brief description of the work, Alarm System Inspections-Visual Inspections and Testing in accordance with NFPA 72 (latest edition) and Alarm Monitoring.

For uniformity, please submit your bid on the Bid Forms included in this Project Manual. All costs and alternatives must be filled in; incomplete bids will be rejected. All bids must be signed.

A bid bond and performance bond is required for project pricing over $100,000.00 annually.

The CDA is exempt from the local .25% transit tax AND the MN state tax of 6.875%. Do not include sales tax in your pricing.

There is one property (Colleen Loney Manor) that is subject to Davis-Bacon prevailing wages and is denoted by “public housing”. It should be noted that the principal contractor is responsible for full compliance of all the workers on-site (the contractor, subcontractors and any lower-tier subcontractors) with the labor standards provisions applicable to the project. Certified weekly payroll will be required to be submitted to CDA offices every week and includes paying construction labor on a weekly basis (a Davis-Bacon requirement).

Contractors or subcontractors that violate the labor standards provisions may face administrative sanction by HUD and/or DOL and may be subject to civil or criminal prosecution.

Contractor requirements:

The Contractor must be able to demonstrate that both the Contractor and its project superintendent have at least three (3) years of experience with projects of this size and type. A list of at least three (3) references and a minimum of three (3) similar projects must be submitted to the CDA upon request.

The Contractor must not be in default on any contracts, must be in compliance with all tax laws of the State of Minnesota, must not be debarred by any institution or government agency as a result of performance of past contracts and must not be in violations of any provisions of contracts with the CDA.

The Contractor must not have been convicted of any criminal offense related to obtaining or attempting to obtain any public or private contract, or subcontract. The Contractor must not have been convicted, under any jurisdiction of law, for embezzlement, theft, forgery, bribery, falsification, or destruction of records, receiving stolen property, or any other offense that, in the opinion of the CDA, is related to business integrity, honesty or performance under contract.

The Contractor must, if so requested by the CDA, submit evidence of ability to obtain the required insurance, must submit references and evidence of compliance with the above requirements within (72) hours of the request.

The Contractor agrees to provide any information requested by the CDA both before and during performance under a contract that the CDA feels is required to verify the Contractor’s compliance with the conditions of the price bid, the requirements of the Project Manual or the conditions of the Contract.

All Dakota County CDA housing sites and developments are tobacco free work zones. No smoking is allowed on the property by guests, staff, or contractors.

The Dakota County Community Development Agency:

The CDA reserves the right to reject any/all price bids received, and to waive any informalities and irregularities in this price bid request.

The CDA reserves the right to reject any contractor that, in the opinion of the CDA, does not meet the listed requirements or is not a responsible or qualified contractor, or does not otherwise have the capability to perform under a contract.

Information supplied to the CDA is subject to the Minnesota Data Privacy Act (MN stat 13.01 et seq) and shall become public unless it falls within one of the exemptions of the Act and is identified as such by the Contractor. The CDA assumes no responsibility to defend any action by a third party seeking to access material deemed to not be public information. The CDA will release any information to comply with a court order. The CDA assumes no responsibility for any damages claimed by a Contractor as a result of release of information provided by the Contractor to the CDA.

Payment requests:

The CDA processes payment requests within (30) days upon electronic receipt emailed to ap@dakotacda.org. Payment requests must have all properly completed paperwork accompanying the request to be processed. The payments to be sent out via USPS, and cannot be picked up.

Change orders:

All change order requests must have the signed authorization, signed both by the Contractor and CDA Authorized Representative, prior to work taking place. Requests for change orders will not be allowed without the proper paperwork.

See the other sections of this RFB for further information and requirements. Also see any other attachments.

Respectfully,

Aaron Davis

Contract Service Coordinator

office:	651-675-4507

fax (new): 651-287-8042

e-mail:	adavis@dakotacda.org

Alarm System Inspections Bid A: Scope of work

TYPES OF SERVICES:

TESTING AND INPECTION OF ALARM SYSTEMS. Includes inspection, testing and reporting of all devices on a schedule determined by the CDA. In addition, system configuration may be required. Schedule must be supplied 14 days prior to work commencing.

REPAIRS, EXTENSIONS, AND NEW INSTALLATION OF EXISTING ALARM SYSTEMS.

Includes the repair, extensions, and new installations of existing systems to meet code and CDA

requirements, on an as-needed basis.

STANDARDS: Testing and documentation shall be conducted and provided as described in NFPA 72 2002 Edition, Chapter 10. Future adopted editions of NFPA shall be applicable and utilized as adopted by the State.

Visual Inspections shall be provided in accordance with NFPA 72 – Section 14.3.1.

Testing procedures shall follow the procedures listed in NFPA 72 – Section 10.4.2.2

All components of the system shall be tested for proper operation in the frequency as described in NFPA 72 – Section 10.4.5.

The components in the annual Inspection and Testing shall include (but is not limited to):

Electrical

- Fire Alarm Panel: Complete testing and evaluation of all control functions of the system

- Test standby power under load conditions

- Perform functional testing of all initiating appliances and devices

- Perform functional testing of all notification/indicating appliances and devices

- Addressable fire alarm systems will have the maintenance logs checked

- Provide electrical test on all flow and tamper switches and PIV devices

- Perform circuit integrity tests

- Perform test and evaluation of all communication equipment

- Perform circuit ground fault tests

- Common area smoke detectors

- Living unit smoke detectors

- Elevator shaft smoke detectors

- Manual pull fire alarms

- Heat detectors

- Heat and smoke detectors in air handling units

- All audible devices

- Fire damper fusible links intact or needing to be replaced

- A full report, as to location of each damper, and whether it is working or not

- Emergency roof hatches (must be physically opened and closed to check operation)

- Magnetic door release

- Kitchen and dining hall air handler alarm and shut off

- Test and verify all annunciation and labeling of the systems

- Verify that all lights are marked right as to location of alert

- Verify daily signal monitoring with the Alarm Monitoring company

- Emergency exit (light) systems

CO Detection Devices

- Tox-Alert carbon monoxide detection (checking and cleaning of all devices)

- Inspection of all CO device settings and recalibration as necessary (replacement shall be with CDA approval only)

- A separate report of all CO detection will be done per building, with all readings and name of equipment and number of devices and their locations

- Verify that all fans and motors operate when Tox-Alert system is activated

- Send written report of inspection and deficiencies to all cities where senior buildings are located within 14 days of inspection completion.

- Provide all NFPA and UL documentation for all required authorities and clients

- Addressable fire alarm systems will have the maintenance logs checked

- Written reports on ALL of the above to be delivered to the CDA within two (2) weeks of inspection

- Written cost estimates of repairs found to be needed from inspection date shall be sent to the CDA within TWO (2) weeks of inspection of each unit

- Properties will be bid, with a separate price for each building, and a grand total

Work must be performed in a manner compliant with all existing state and local safety laws, rules, regulations, and standards including, but not limited to OSHA, to ensure the safety of the workers, as well as the general public. All work must be conducted so as to interfere, as little as possible, with our residents and staff.

LIFE SAFETY SYSTEM LOG BOOK. All service records shall be recorded and kept and shall serve as a reference tool for local authorities, insurance carriers, and technical personnel.

REGULATIONS. The Contractor shall provide system testing, inspection, repairs, and documentation as prescribed by NFPA standards, the Joint Commissions standards, local, city, and State codes, and insurance companies’ requirements. Testing, inspection, cleaning, sensitivity testing, and repairs of fire alarm system shall satisfy the requirements of NFPA, shall conform to the equipment manufacturer’s recommendations, and shall verify correct operation of the system.

REPORTS. The Contractor shall be responsible for maintaining a permanent and electronic record and inventory of all inspections and testing activities. The records shall be maintained for minimum period of three (3) years following the previous inspection and testing activities. All reports must be sent to the CDA CSM within 14 days after the inspections are completed.

Inspection reports shall be of a typed nature and electronically maintained per building. The reports must comply with the NFPA and Joint Commission requirements. Contractor will be responsible to notify and clarify any concerns from the inspection with the Contract Services Manager. Within two (2) weeks of the inspection, the Contractor shall provide a copy of the inspection report electronically by email to the Contract Services Manager. Fire alarm reports must indicate the location of each peripheral device, address/zone and test results.

Additionally, the following sites:

The Dakotah, Haskell Court, River Heights Terrace, Thompson Heights, Dakota Heights, and CLM are required (by South Metro Fire) to be reported electronically with their compliance partner Brycer, LLC., at https://www.thecomplianceengine.com/ 630-413-9511, e-mail questions at support@mybrycer.com

Any deficiencies noted that are critical to the system components that may result in system impairment or high risk shall be provided to the facility before the end of the business day in which the defect was found. Examples of high-risk deficiency shall include fire alarm system devices that will not allow a fire alarm signal to be received at the off-site Central Monitoring facility. Critical system components requiring repair or replacement shall be provided to the CDA within twenty-four (24) hours of the finding.

The report, at a minimum, shall include the following:

- Summary of the test

- Date of testing, description of devices tested, location of each device within the building

- Test results for the Alarm Initiating Devices

- Test results for the Fire Alarm Control Panels

- Deficiencies Noted and corrective action taken or recommended

- Monitoring/Jurisdictional Agencies noted or informed

- List monitoring panel and peripherals—building name; address; monitoring company; monitoring company; account #; panel manufacturer; battery voltage, after AC loss, after in alarm AC loss, battery dates; heat detectors; smoke detectors; sprinkler system tapers, low pressure switches, high pressure switches; outside audio/visual, horns, strobe/horns; signaling devices, strobes, bells, speakers, mini-horns; elevator capture; fire door/door holders; smoke dampers & controls

- List Smoke/fire dampers & locations

- List Area of Refuge—speaker, microphone, and LED function

- List Garage Exhaust & CO Detection

The service report shall also include the repair services detailing the purpose of the call, location and description of work completed, and list of parts repaired/replaced.

Provide the reports in a printed format (send via USPS), and in a .pdf format (send via e-mail).

The fire alarm Contractor shall provide all tools, lifts, and materials needed to perform inspections, testing, installation, repairs and extensions of systems.

Contractor shall be responsible for coordinating and notifying the CDA’s monitoring company prior to and at the conclusion of all testing.

The Contractor shall be responsible for notifying the CDA representative of all revisions to the fire alarm equipment types and quantities as they are identified during the term of the Contract. All information shall be provided in writing as soon as possible (after the revision or finding) to the CDA.

TEST AND INSPECTION REQUIREMENTS.

A. Functional Testing of Peripheral Devices: In accordance with all NFPA requirements, NFPA 72, Joint Commission and manufacturer’s recommendations, all accessible and some non-accessible peripheral devices shall be functionally tested and inspected and reported

Smoke Detectors: Shall be functionally tested using only UL approved smoke generators.

Heat Detectors: Shall be tested for rate of rise and shall be tested using UL approved Heat Tester device that administers an accurate and controlled temperature heat source per the manufacturer’s recommendations for a response within 1 minute. The test method used must not damage the non-restorable fixed temperature element of a combination rate of rise/fixed temperature element detector.

Fixed temperature non-restorable line type heat detectors shall be tested electronically and mechanically for functionality.

Manual Pull Stations: Shall be opened and verify operation and inspected to ensure secure mounting. Also test tamper devices and report findings.

Audible and Visible Signaling Devices: Shall be tested at least once per year to ensure proper operation and volume levels.

Duct Detectors: Shall be tested routinely, or at a minimum annually, on a schedule determined by the CDA. If the duct detector’s sensitivity is within specifications, nothing further needs to be done to the detector. If the duct detector’s sensitivity is outside specifications, replace the detector upon approval from the CDA Representative and follow the manufacturer’s recommended procedure.

Fire Dampers, Smoke Dampers & Fire/Smoke Dampers: Shall be tested every year (which exceeds code requirements--at least every 4 year) or on a schedule determined by the CDA representative. Testing shall include operation of the dampers to ensure that they fully close, removal of fusible links, a check of latches, if provided, and lubrication of all moving parts as necessary. Any repairs made shall be also recorded and shared with the Contract Services Manager.

SMOKE MANAGEMENT SYSTEMS. In accordance with NFPA 92B, the system shall be tested at least semi-annually by persons who are thoroughly knowledgeable in the operation, testing, and maintenance of the systems. The schedule shall be determined by the CDA to ensure that each of the components of the system is working correctly and that they work together as a system according to design intent and governing codes. Testing shall include all equipment, such as initiating devices, fans, dampers, controls, doors, and windows. The equipment shall be maintained in accordance with the manufacturer’s recommendations. The periodic tests shall determine the airflow quantities and the pressure differences at the following locations:

- Across smoke barrier openings;

- At the air makeup supplies;

- At smoke exhaust equipment.

All data points shall coincide with the acceptance test location to facilitate comparison measurements. Test shall also be conducted under standby power if applicable. Special arrangements shall be considered for the introduction of large quantities of outside air into occupied area or computer centers when outside temperature and humidity conditions are extreme and when such unconditioned air could damage contents. The results shall be documented in the operations and maintenance log and make available for inspection.

ADDITIONAL SERVICES (TO BE INCLUDED IN YOUR BASE PRICING)

Smoke Detector Cleaning: To help minimize false alarms and maximize detector accuracy, accessible smoke detection devices shall be cleaned utilizing manufacturer’s recommended procedures. Devices will be dismantled to expose the smoke chamber (where applicable) and cleaned in conjunction with sensitivity testing using soft cloth, lint brush, or non-electrostatic vacuum to prevent damage due to static electricity.

Sensitivity Testing: To help ensure accuracy, non-addressable smoke detectors shall be tested for proper sensitivity rating per NFPA 72. Testing shall be performed using only a UL approved sensitivity tester. Devices performing outside the listed sensitivity range shall be re-cleaned and re-tested, and if

necessary, recommended for replacement. Note: certain types of analog smoke sensors automatically satisfy this requirement electronically.

Duct Detector Cleaning: Cleaning shall be done by using a vacuum cleaner to remove dust from the detector by placing the nozzle as close as possible to the openings in the outside housing. A nozzle with a brush attachment will assist in dust removal. Some smoke detectors can be removed for more thorough cleaning; refer to manufacturer’s recommended procedure for details. Also check the sampling tube holes and filters to make sure they are not clogged.

TESTING OF PANEL COMPONENTS AND PANEL FUNCTIONS. In accordance with NFPA 72 and

manufacturer’s recommendations, all panel components shall be tested and documented for proper function. This includes all applicable input and output voltage readings, LED and lamp test, and all alarm and trouble circuits. For hardwire systems, all devices shall be logged for proper zone verification. All addressable devices for addressable systems will be logged for proper address verification and annunciator location information verified. Batteries shall be checked for age, and shall be load tested to ensure proper charging and adequate power capacity with a UL approved load tester. Additionally, all auxiliary relays shall be tested for correct operation (such as interfaces for elevator recall and smoke dampers). Central station monitoring dialer or communicators shall be tested and documented. Local authorities and central monitoring stations shall be contacted prior to testing and upon completion of work.

REPAIRS, EXTENSIONS AND NEW INSTALLATION OF FIRE ALARM SYSTEMS.

- Shall be in accordance   with   NFPA   72   and   Joint   Commissions   standards, local, city, and   state   codes   and

manufacturer’s recommendations. All parts shall be OEM if required to maintain the system’s UL rating

(if applicable).

- The CDA CSM shall be responsible for determining if and/or when any additional work will be

performed. The CDA CSM reserves the right to either have the test and inspection contractor make the

repair or solicit quotes for the repair from other contractors.

- Repair, extensions and new installation of fire alarm systems will be quoted using contract hourly rates

and cost-plus mark-up for materials including shipping. Agencies shall request written itemized quotes

prior to proceeding.

- Repairs shall include, at a minimum, Contractor’s one-year warranty on the work, including all labor

and materials.

- Contractor shall not proceed with any repair/service:

  - without authorization or a Purchase Order/Work Order issued from the CDA CSM

  - without a schedule that has been agreed upon with the CDA CSM

- Contractor shall not exceed the amount which is on the Purchase Order/Work without written approval

from the CDA CSM.

- If the Contractor proceeds without a purchase order/work order or exceeds the purchase order amount

without written approval from the CDA CSM, the Contractor may not be paid for the repair/service.

- The Contractor shall have an inventory available of common repair parts stocked within the serving

technician’s vehicles. All parts replaced must be compatible with the existing system and UL approved.

- Wiring: Shall be by the appropriate contractor for the type of wiring required.

CYCLE OF TESTING, REPORTING AND REPAIRS (SEE THE ATTACHED BID FORM)

See the bid form for all sites to be included in this Contract and served.

An abbreviated summary is:

(28) Senior buildings

(4) Family sites that fire sprinkler systems and fire reporting panels: (Lafayette, Keystone, Prestwick and Denmark).

(1) Youth Supportive Housing site (Lincoln Place).

(1) Singles (Gateway Place)

(1) Veterans Building (Nicols Pointe)

(1) Main Office building.

(1) Public Housing development (CLM).

Alarm Monitoring Bid B: Scope of Work:

The Contractor shall provide monitoring of all buildings with the exception of Eagle Ridge Place and Park Ridge Place Senior Buildings (see alternates). The Contractor must include the changing of monitoring phone numbers in their bid. The CDA will not pay separately or any additional charges for the changeover of phone numbers.

The equipment at each site is listed on the Bid Form. The Contractor shall use the existing equipment unless it is defective or proprietary. If the equipment is proprietary, then it will be replaced with equipment listed below and monitoring will follow the parameters listed below:

- A Silent Knight 5104B (by Honeywell), or equivalent fire communicator panel must be used, providing at least 6 zones supervised fire zones consisting of one class A (style D) and five Class B (style B) zones. The manual must be left on site for owners use. No proprietary equipment shall be used. Contractor must submit and get CDA written approval for any equivalent proposed.

- Monitoring company must receive a supervised daily test from each site.

- Bid shall include one (1) physical test/inspection per site/per year.

- Copy of test shall be sent to the CDA annually.

- The dialer panel must have a dedicated battery backup system (with a battery provided).

- Dialer panel battery backup shall be replaced each year in the base contract—24-hour battery backup from a 12-volt DC and amp hour rechargeable battery.

- The installer code must be programmed as instructed by the CDA.

- The monthly monitoring fee shall be guaranteed for the contract time period. No other fees shall apply other than routine service that may be needed.

- One-year parts & labor warranty on all new equipment.

- There shall be no pro-ration of any individual component or unit. The Contractor shall take the equipment “as is”.

- Monitoring company must have account information/history accessible to the CDA by means of the web. The CDA needs to be able to access all accounts on a 24-hour basis.

- Included in this Contract will be the CDA Office Fire Safety Monitoring and the Office Security System Monitoring.

- If work is required or requested by the CDA outside the scope of this agreement, the CDA will pay for labor at the hourly rates indicated hereafter.

Section 3 Requirements

(applies to all CDA sites)

The work to be performed under this Contract is subject to the requirements of Section 3 of the Housing and Urban development Act of 1968, as amended, 12 U.S.C. 170lu (section 3). The purpose of Section 3 is to ensure that employment and other economic opportunities generated by HUD assistance or HUD-assisted projects covered by Section 3, shall, to the greatest extent feasible, be directed to low- and very low-income persons, particularly persons who are recipients of HUD assistance for housing.

The parties to this Contract agree to comply with HUD’s regulations in 24 CFR part 135, which implement Section 3. As evidenced by their execution of this Contract, the parties to this Contract certify that they are under no contractual or other impediment that would prevent them from complying with the part 135 regulations.

The Contractor agrees to send to each labor organization or representative of workers with which the Contractor has a collective bargaining agreement or other understanding, if any, a notice advising the labor organization or workers’ representative of the Contractor’s commitments under this Section 3 clause, and will post copies of the notice in conspicuous places at the work site where both employees and applicants for training and employment positions can see the notice. The notice shall describe the Section 3 preference, shall set forth minimum number and job titles subject to hire, availability of apprenticeship and training positions, and qualifications for each; the name and location of the person(s) taking application for each of the positions; and the anticipated date the work shall begin.

The Contractor agrees to include this Section 3 clause in every subcontract subject to compliance with regulations in 24 CFR part 135, and agrees to take appropriate action, as provided in an applicable provision of the subcontract or in this Section 3 clause, upon a finding that the subcontractor is in violation of the regulations in 24 CFR part 135. The Contractor will not subcontract with any subcontractor where the Contractor has notice or knowledge that the subcontractor has been found in violation of the regulations in 24 CFR part 135.

The Contractor will certify that any vacant employment positions, including training positions, that are filled (1) after the Contractor is selected but before the Contract is executed, and (2) with persons other than those to whom the regulations of 24 CFR part 135 require employment opportunities to be directed, were not filled to circumvent the Contractor’s obligations under 24 CFR part 135.

Noncompliance with HUD’s regulations in 24 CFR part 135 may result in sanctions, termination of this Contract for default, and debarment or suspension from future HUD assisted Contracts.

With respect to work performed in connection with Section 3 covered Indian Housing Assistance, Section 7(b) of the Indian Self-Determination and Education Assistance Act (25 U.S.C. 450e) also applies to the work to be performed under this Contract. Section 7(b) requires that to the greatest extent feasible (1) preference and opportunities for training and employment shall be given to Indians, and (2) preference in the award of contracts and subcontracts shall be given to Indian organizations and Indian-owned Economic Enterprises. Parties to this contract that are subject to the provisions of Section 3 and Section 7(b) agree to comply with Section 3 to the maximum extent feasible, but not in derogation of compliance with Section 7(b).

See attached HUD 60002 form.  This form to be completed by the contract holder(s).

Alarm System Inspection

BID FORM A

Forward to:

Dakota County CDA

Attn: Aaron Davis

1228 Town Centre Drive

Eagan, Minnesota 55123

- Base Price (per site):

The undersigned, having carefully examined the Project Manual prepared by The Dakota County CDA for the following work:

Emergency System Inspection (Dakota CDA), Minnesota, being familiar with the local conditions affecting the cost of the work, hereby proposes to furnish all labor, material, equipment, tools, transportation, taxes and services necessary to complete the work. The Davis–Bacon labor rates are to be applied to public housing sites. Work to be in accordance with the Project Manual for the following sums:

- Dakota County CDA Office Building Alarm & Burglar System Inspections 1228 Town Centre Drive

Eagan, MN 55123	Subtotal

- Colleen Loney Manor (public housing; Davis-Bacon wages) 1675 Livingston Ave.

West St.Paul, MN 55118

(77) one bedrooms, 3 two bedrooms; (80 total);

Ansul System	Subtotal

- Winsor Plaza

20827 Howland Avenue

Lakeville, MN 55044

  - one bedrooms, (20) two bedrooms; (64 total)

Air dryer desiccant, Fire Pump, Ansul System	Subtotal

- Oakwoods of Eagan 2065 Park Center Drive Eagan, MN 55122

  - one bedrooms (3 HC units), 21 two bedrooms, (65 total)

Air Dryer Desiccant	Subtotal

- Haskell Court

140 East Haskell

West St. Paul, MN 55118

(27) one bedrooms (2 HC), (15) two bedrooms; (42 total)	Subtotal

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Mississippi Terrace

301 Ramsey St.

Hastings, MN 55033

(27) one bedrooms (2 HC), (13) two bedrooms; (40 units)

Air dryer desiccant	Subtotal

- Carmen Court

5825 Carmen Ave

Inver Grove Heights, MN

(33) one bedrooms (2 HC), (18) two bedrooms; (51 total)

Air dryer desiccant	Subtotal

- Orchard Square

7375-157th Street West Apple Valley, MN

(32) one bedrooms (2 HC), 18 two bedrooms; (50 total)

Air dryer desiccant	Subtotal

- River Heights Terrace 1720 Thompson Avenue South St. Paul, MN 55075

(34) one bedrooms (2 HC), (20) two bedrooms; (54 total)

Air dryer desiccant	Subtotal

- Parkview Plaza

730 South Plaza Drive Mendota Heights, MN 55120

(42) one bedrooms (2 HC), (23) two bedrooms; (65 units)	Subtotal

- Cameo Place

3101 Lower 147th Street Rosemount, MN 55068

(30) one bedrooms (2 HC), (14) two bedrooms; (44 units)	Subtotal

- O’Leary Manor

1220 Town Center Drive Eagan, MN 55123

(38) one bedrooms, (27) two bedrooms; (65 units)	Subtotal

- Cortland Square 7385-157th Street

Apple Valley, MN 55124

(41) one bedrooms (2 HC), 19 two bedrooms; (60 total)	Subtotal

- Main Street Manor 8725 209th Street West Lakeville, MN 55044

(34) one bedrooms, (17) two bedrooms; (51 total)	Subtotal

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Cahill Commons 5840 Cahill Avenue

Inver Grove Heights, MN 55075

(38) one bedrooms, (22) two bedrooms; (60 total)	Subtotal

- Village Commons 720 Linden Street

Mendota Heights, MN 55118

- one bedrooms, (30) two bedrooms; (60 total)	Subtotal

- Lakeside Pointe

1200 Town Centre Drive Eagan, MN 55123

(32) one bedrooms, (28) two bedrooms; (60 total)	Subtotal

- The Dakotah

900 South Robert Street West St. Paul, Mn. 55118

(48) one bedrooms, (11) two bedrooms, (59 total)	Subtotal

- Rivertown Court

1791 South Frontage Rd.

Hastings, MN 55033

(38) one bedrooms, (25) two bedrooms; (63 total)

Fire pump	Subtotal

- Argonne Hills 17688 Junelle Path

Lakeville, MN 55044

(36) one bedrooms, (26) two bedrooms; (62 units)

No range hood system, area of refuge	Subtotal

- Dakota Heights

337-15th Ave. North South St. Paul, MN 55075

- one bedrooms, (25) two bedrooms; (56 total)

Ansul System	Subtotal

- Oakwoods East

2061 Park Center Drive Eagan, MN 55122

(29) one bedrooms (1 HC), (26) two bedrooms; (55 total)

Area of refuge	Subtotal

- Crossroads Commons 17725 Glasgow Ave.

Lakeville, MN 55044

(45) one bedrooms (1 HC), (42) two bedrooms; (87 total)

Ansul system, area of refuge, fire pump	Subtotal

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Cobblestone Square 15848 Emperor Ave.

Apple Valley, MN 55124

(30) one bedrooms, (30) two bedrooms; (60 total)

Ansul system, area of refuge	Subtotal

- Thompson Heights 1350 Thompson Ave.

South St. Paul, MN 55075

(30) one bedrooms (3HC), (30) two bedrooms; (60 units)

Ansul system, Area of refuge	Subtotal

- Vermillion River Crossing 21400 Dushane Parkway

Farmington, MN 55024

- one bedrooms, (34) two bedrooms; (66 units)

Ansul system, area of refuge	Subtotal

- Hillcrest Pointe 9170 Cahill Ave.

Inver Grove Heights, MN 55075

(32) one bedrooms, (34) two bedrooms; (66 units)

Ansul system, area of refuge (8 zones)	Subtotal

- Cambrian Commons 14736 Cambrian Ave,

Rosemount, MN 55068

(34) one bedrooms, (26) two bedrooms; (60 units)

No range hood system, area of refuge	Subtotal

- Lincoln Place 1997 Gold Trail

Eagan, MN 55122

(24) studio units, Area of refuge

(1) one-bedroom unit; (25 total)	Subtotal

- Keystone Crossing Townhomes 20688-20696 Keystone Ave.

Lakeville, MN 55044

(21) two bedrooms, (2) two bedrooms HC,

(13) three bedroom—townhome units	Subtotal

- Prestwick Townhomes 14101-14160 Addison Way

Rosemount, MN 55068 (40 units)

(6) one bedroom, (19) two bedroom, (2) two bedroom HC,

(13) three bedroom—townhome units	Subtotal

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Lafayette Townhomes

4900 Bongard Way

Inver Grove Heights, MN 55076

(30) townhome units, several sprinkler room locations	Subtotal

- Denmark Townhomes

Denmark Trail, Farmington MN  55024

(40) townhome units, several sprinkler room locations		Subtotal

- Nicols Pointe

4012 Nicols Rd

Eagan, MN 55

(24) 1 bedroom units	Subtotal

Alarm System Inspection

Total of all the above sites listed for one year--2026	Total

Total second (2nd) year--2027	Total

Total third (3rd) year--2028	Total

- Alternates:

Alternates must be filled out to be a completed/valid form. Price for work includes: to be done during regular work hours (not overtime), trip to site, taxes and any permits. Prices for alternates to be maintained for years 1-3 of the contract period unless otherwise noted.

The prices of the Alternates are extra accessory costs, and thus have no bearing in the requirements for requiring a bid bond or performance and payment bond. Only the base price will have bearing on the bonding requirements. The alternates will have “weight” in the award of this Contract, and to be determined by CDA staff. There will be no allowance for charges unless previously approved by the CDA.

Th price of a truck charge will be capped at $40 per repair for a single visit. All gas charges, extra surcharges or taxes.

  - Eagle Ridge Place

12600 Eagle Ridge Drive Burnsville, MN 55337

(37) one bedrooms (2 HC units), (23) two bedrooms; (60 total)

Air dryer desiccant, UL Rating monitoring & inspection to be done together. Add $	dollars/per year

  - Park Ridge Place

330 East Burnsville Parkway Burnsville, MN 55337

(46) one bedrooms (2 HC), (20) two bedrooms; (66 total)

UL Rating monitoring & inspection to be done together.

Add $	dollars/per year

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

  - Provide a price for the replacement of a Kidde brand smoke detector, or comparable substitute approved by CDA Contract Services Manager (includes all costs).

Add $	dollars

  - Add/Remove (1) smoke detector equipment for Smoke Detector Battery Replacement (price for replacing a 9V alkaline battery in a smoke detector).

Add/Delete	$		per battery / per smoke detector

  - Provide a price for a new Kidde brand smoke detector, or comparable substitute approved by CDA Contract Services Manager (includes all costs).

Add $	dollars

  - Cost-plus mark-up for alternate materials (not listed in the alternates 3-5).

| a. First Year (2026) | % | mark-up |
| --- | --- | --- |
| b. Second Year (2027) | % | mark-up |
| c. Third Year (2028) | % | mark-up |

  - Hourly rate for repair labor work (not listed in the alternates 3-5).

| a. First Year (2026) | $ | per hour |
| --- | --- | --- |
| b. Second Year (2027) | $ | per hour |
| c. Third Year (2028) | $ | per hour |

There may be other items added to contract at a later date, but they will be bid separately and may be added to contract and terminate when the contract terminates.

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

ALARM MONITORING BID FORM B

Forward to:

Dakota County CDA Attn: Aaron Davis

- Base Price (per site):

The undersigned, having carefully examined the Project Manual prepared by The Dakota County CDA for the following work:

Alarm Monitoring (Dakota CDA), Minnesota, being familiar with the local conditions affecting the cost of the work, hereby proposes to furnish all labor, material, equipment, tools, transportation, taxes and services necessary to complete the work. The Davis–Bacon labor rates are to be applied to public housing sites (CLM only). Work to be in accordance with the Project Manual for the following sums:

  - Dakota County CDA Main Office 1228 Town Centre Drive

Eagan, MN 55123

DSC MAXSYS PC 4204CF	Subtotal	/month

  - Colleen Loney Manor (public housing) 1675 Livingston Ave.

St. Paul, MN 55118

(77) one bedroom, 3 two bedroom; (80 Subtotal);

Silent Knight 5104	Subtotal	/month

  - Winsor Plaza

20827 Howland Avenue

Lakeville, MN 55044

(44) one bedroom, (20) two bedroom; (64 Subtotal)

Silent Knight 5104	Subtotal	/month

  - Eagle Ridge Place

12600 Eagle Ridge Drive Burnsville, MN 55337

(37) one bedrooms (2 HC units), (23) two bedrooms; (60 Subtotal) UL Rating monitoring & inspection to be done together

Silent Knight 5104	See Alternates

  - Oakwoods of Eagan 2065 Park Center Drive Eagan, MN 55122

(44) one bedroom (3 HC units), 21 two bedrooms, (65 Subtotal)

Silent Knight 5104	Subtotal	/month

  - Haskell Court

140 East Haskell

West St. Paul, MN 55118

(27) one bedroom (2 HC), (15) two bedroom; (42 Subtotal)

Silent Knight 5104	Subtotal	/month

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

| Mississippi Terrace |  |  |
| --- | --- | --- |
| 301 Ramsey St. |  |  |
| Hastings, MN 55033 |  |  |
| (27) one bedroom (2 HC), (13) two bedroom; (40 units) |  |  |
| Silent Knight 5104 | Subtotal | /month |
| Carmen Court 5825 Carmen Ave |  |  |
| Inver Grove Heights, MN |  |  |
| (33) one bedroom (2 HC), (18) two bedroom; (51 Subtotal) |  |  |
| Radionics D7412G | Subtotal | /month |

​

  - ​

  - Orchard Square

7375-157th Street West Apple Valley, MN

(32) one bedroom (2 HC), 18 two bedrooms; (50 Subtotal)

Silent Knight 5104	Subtotal	/month

  - River Heights Terrace 1720 Thompson Avenue South St. Paul, MN 55075

(34) one bedrooms (2 HC), (20) two bedrooms; (54 Subtotal)

FACP	Subtotal	/month

  - Parkview Plaza

| 730 South Plaza Drive Mendota Heights, MN 55120 (42) one bedroom (2 HC), (23) two bedroom; (65 units) Silent Knight 5104 | Subtotal | /month |
| --- | --- | --- |
| 12. Cameo Place |  |  |
| 3101 Lower 147th Street |  |  |
| Rosemount, MN 55068 |  |  |
| (30) one bedroom (2 HC), (14) two bedroom; (44 units) |  |  |
| Silent Knight 5104 | Subtotal | /month |
| 13. O’Leary Manor |  |  |
| 1220 Town Center Drive |  |  |
| Eagan, MN 55123 |  |  |
| (38) one bedroom, (27) two bedrooms; (65 units) |  |  |
| Silent Knight 5104 | Subtotal | /month |

- Park Ridge Place

330 East Burnsville Parkway Burnsville, MN 55337

(46) one bedroom (2 HC), (20) two bedrooms; (66 Subtotal)

Silent Knight 5104	See Alternates

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

| 15. Cortland Square |  |  |
| --- | --- | --- |
| 7385-157th Street |  |  |
| Apple Valley, MN 55124 |  |  |
| (41) one bedroom (2 HC), 19 two bedroom; (60 Subtotal) |  |  |
| Edwards LSS4/20 | Subtotal | /month |
| 16. Main Street Manor |  |  |
| 8725 209th Street West |  |  |
| Lakeville, MN 55044 |  |  |
| (34) one bedroom, (17) two bedrooms; (51 Subtotal) |  |  |
| Silent Knight 5128 | Subtotal | /month |
| 17. Cahill Commons |  |  |
| 5840 Cahill Avenue |  |  |
| Inver Grove Heights, MN 55075 |  |  |
| (38) one bedroom, (22) two bedroom; (60 Subtotal) |  |  |
| Silent Knight 5129 18. Village Commons | Subtotal | /month |
| 720 Linden Street |  |  |
| Mendota Heights, MN 55118 |  |  |
| (30) one bedroom, (30) two bedroom; (60 Subtotal) |  |  |
| Silent Knight 5104 | Subtotal | /month |
| 19. Lakeside Pointe 1200 Town Centre Drive |  |  |
| Eagan, MN 55123 |  |  |
| (32) one bedroom, (28) two Bedrooms; (60 Subtotal) |  |  |
| Silent Knight 5104 | Subtotal | /month |
| 20. The Dakotah 900 South Robert Street |  |  |
| West St. Paul, MN 55118 |  |  |
| (48) one bedroom, (11) two bedroom, (59 Subtotal) |  |  |
| Silent Knight 5128 | Subtotal | /month |
| 21. Rivertown Court 1791 South Frontage Rd. |  |  |
| Hastings, MN 55033 |  |  |
| (38) one bedroom, (25) two bedroom; (63 Subtotal) |  |  |
| G.W. UDACT | Subtotal | /month |
| 22. Dakota Heights |  |  |
| 337-15th Ave. North |  |  |
| South St. Paul, MN 55075 |  |  |
| (31) one bedroom, (25) two bedrooms; (56 Subtotal) |  |  |
| UDACT (Honeywell) | Subtotal | /month |

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Oakwoods East

| 2061 Park Center Drive Eagan, MN 55122 (29) one bedroom (1 HC), (26) two bedroom; (55 Subtotal) Silent Knight 5808 | Subtotal | /month |
| --- | --- | --- |
| Oakwoods East Area of Refuge | Subtotal | /month |

- Crossroads Commons

17725 Glasgow Ave.

Lakeville, MN 55044

(45) one bedroom (1 HC), (42) two bedroom; (87 Subtotal)

Silent Knight 5820 XL	Subtotal	/month

| 15848 Emperor Ave. |  |  |
| --- | --- | --- |
| Apple Valley, MN 55124 |  |  |
| (30) one bedroom, (30) two bedroom; (60 Subtotal) |  |  |
| DACT (Honeywell) | Subtotal | /month |
| Thompson Heights 1350 Thompson Ave. |  |  |
| South St. Paul, MN 55075 |  |  |
| (30) one bedroom (3HC), (30) two bedroom; (60 units) |  |  |
| Allied Telesis AT-IMG 824 | Subtotal | /month |
| Vermillion River Crossing 21400 Dushane Parkway |  |  |
| Farmington, MN 55024 |  |  |
| (32) one bedroom, (34) two bedroom; (66 units) |  |  |
| Mircom FX2000 | Subtotal | /month |
| Vermillion River Crossing Area of Refuge | Subtotal | /month |

Cobblestone Square

- ​

- ​

- Hillcrest Pointe

9170 Cahill Ave.

Inver Grove Heights, MN 55075

(32) one bedroom, (34) two bedroom; (66 units) Ansul system, area of refuge (8 zones)

Mircom FXX-3500	Subtotal	/month

- Cambrian Commons

14736 Cambrian Ave,

Rosemount, MN 55068

(34) one bedroom, (26) two bedroom; (60 units) No range hood system, area of refuge

Simplex 4100	Subtotal	/month

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Argonne Hills

17688 Junelle Path

Lakeville, MN 55044

(36) one bedroom, (26) two bedroom; (62 units)

No range hood system	Subtotal	/month

Simplex 4100

Argonne Hills Area of Refuge	Subtotal	/month

- Gateway Place

895 South Robert Street

West St. Paul, MN 55118 (54 Units) Mixed studio and one bedroom

Silent Knight 6808	Subtotal	/month

Gateway Place Area of Refuge 	Subtotal	/month

- Lincoln Place

1997 Gold Trail

Eagan, MN 55122

(24) studio units, (1) one bedroom

Silent Knight with addressable panel DACT dialer	Subtotal	/month

- Nicols Pointe

4012 Nicols Rd

Eagan, MN 55

(24) 1 bedroom units

Silent Knight 6808	Subtotal	/month

- Keystone Crossing Townhomes 20688-20696 Keystone Ave.

Lakeville, MN 55044

(21) two bedroom, (2) two bedroom HC, (13),

(13) three bedroom—townhome units	Subtotal	/month)

Silent Knight 5700

- Lafayette Townhomes

4900 Bongard Way

Inver Grove Heights, MN 55076

(30) townhome units, several sprinkler room locations

DSC DC4020CF	Subtotal	/month

- Prestwick Townhomes

14101-14160 Addison Way

Rosemount, MN 55068 (40 units)

(6) one bedroom, (19) two bedroom,

(2) two bedroom HC,(13) three bedroom	Subtotal	/month

Edwards panel

- Denmark Trail Townhomes Denmark Ave.

Farmington, MN 55024 (40 Units) 				Subtotal_____________/month

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

| Subtotal of all the above sites listed for (1st) year—2026 | Total | /1st year |  |
| --- | --- | --- | --- |
| Subtotal second (2nd) year—2027 | Total | /2nd year |  |
| Subtotal third (3rd) year—2028 | Total | /3rd year |  |
| COMBINE TOTALS FROM BID FORM A AND BID FORM B: |  |  |  |
| Total of all the above sites listed for (1st) year—2026 | Total | /1st year |  |
| Total second (2nd) year—2027 | Total | /2nd year |  |
| Total third (3rd) year—2028 | Total | /3rd year |  |
| Alternates: |  |  |  |

- Add (1) site for Monitoring (price for an operating line & monitoring).

Add/Delete	$		per line per Month

- Add (1) site Wireless Communicator (price for an operating line & monitoring).

Add/Delete	$		per line per Month

- Add (1) site of Area of Refuge Monitoring (price for an operating line & monitoring).

Add/Delete	$		per line per Month

- Add (1) site VOIP—voice over internet protocol (price for an operating line & monitoring).

Add/Delete	$		per line per Month

- Repair technician. Straight Time (regular working hours).

Add	$		per hour

- Repair technician. Overtime.

Add	$		per hour

- Repair technician. Weekend.

Add	$		per hour

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Repair technician. Holiday.

Add	$		per hour

- Repair technician. Increase per year after year 1

  - 2nd year 	%

  - 3rd year 	%

GENERAL (Alarm Systems Inspections & Alarm Monitoring)

    - Accompanying this bid is a bid security in the form of a 	in the amount of

$	. The bid security noted above includes the combination total of the base bid plus the total of all alternates. The undersigned agrees that if this bid is accepted and the undersigned refuses to enter into a Contract with the CDA on the terms stated in this Bid or fails to furnish satisfactory Performance and Payment Bonds in accordance with the Bidding Documents, this bid security shall be forfeited to the CDA, not as a penalty, but as liquidated damages.

    - The undersigned agrees, if awarded the Contract, to enter into a Contract with the CDA and will execute the Agreement and furnish satisfactory Performance and Payments Bonds in accordance with the Bidding Documents.

    - The undersigned agrees that this bid may not be withdrawn for a period of (60) calendar days immediately following the date of receipt of bids. It is understood that the CDA reserves the right to reject any or all bids, to waive any informality or irregularity in any bid received and to accept any alternate in any order or combination.

    - Addenda Nos. 	have been received and incorporated in this Bid. (required to be filled in)

    - I have reviewed the site conditions, the project manual, requirements, and submittals in providing the costs for the noted services:

Date

Company

Name		 (Signature)

Name		 (Printed Name)

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

## CONTRACTOR’S QUALIFICATION STATEMENT

(Submit this form as part of bid response)

SUBMITTED BY		CORPORATION

ADDRESS		PARTNERSHIP

PRINCIPAL OFFICE		INDIVIDUAL

PHONE		OTHER

(NOTE: Attach separate sheets as necessary)

      - How many years has your organization been in business?

      - How many years has your organization been in business under its present business name?

3: If a corporation answer the following: Date of incorporation:

State of incorporation:

President’s name:

Vice-President’s name:

Secretary’s name:

Treasurer’s name:

- If individual or partnership, answer the following: Date of organization:

Name and address of all partners:

- We normally perform 	% of the work with our own forces;

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA

- Have you ever failed to complete any work awarded to you? If so, note when Where, and why:

- List the construction experience of the principal individuals of your organization:

- List your principal subcontractors:

- List your principal suppliers:

- List your bank references:

- List three completed projects who may be contacted as references, type or work address, phone number and contact name.

1.

2.

3.

- List insurance requirements Name of Insurance company:

Name of Insurance agent:

Agents phone number:

- Are you licensed by the State of Minnesota?

List other licenses held:

I certify that the above is true and complete and I authorize the Dakota County CDA to verify any information on this statement.

Signature	Date

REQUIRED BID SUBMITTAL DOCUMENT – MUST TO RETURNED TO CDA